| System | TX 01 Main Power Transformer |
| --- | --- |
| Aim | Electrical-Online Aim |
| Site or Area | Substation 101 |
| Location | Bay 201 |
| Equipment Condition | Online |
| Instructions | The tasks listed in this document are to be carried out while the equipment is online. WARNING: Never touch moving or energized equipment. |
| Special Notes |  |
| Hazards | Chemical Substances Operating Machinery, Moving Parts, Pinch Points, Electrocution, Tripping & Slipping Hazards, Ergonomic Issues |
| Permits and Isolations | Job Hazard Assessment or Safety Risk Assessment Always make sure your supervisor knows where you are working or what equipment you are servicing |
| Personal Protective Equipment (PPE) | Standard Site PPE |
| Other Safety Equipment |  |
| Tools | Standard Trade Tools |
| Materials |  |
| Resources | 2 Electrical |
| References |  |
| Prepared By | Your Name Goes Here |

| JSA - Job Safety Assessment |  |
| --- | --- |
| TASK | DESCRIPTION |
| 1 | Analyse all conditions on site. Pay particular attention to changes since the previous day or shift. |
| 2 | Write down all risks |
| 3 | Determine and implement appropriate controls |
| 4 | Explain to all team members and sign. |

|  | Name | Date | Signature |
| --- | --- | --- | --- |
| 1 |  |  |  |
| 2 |  |  |  |
| 3 |  |  |  |
| 4 |  |  |  |
| 5 |  |  |  |

| SIL - Silica Gel Inspection |  |
| --- | --- |
| TASK | DESCRIPTION |
| 1 | Inspect colour of silica gel. Compare discolouration with chart. |

| WIR - Wiring Inspection |  |
| --- | --- |
| TASK | DESCRIPTION |
| 1 | Visually and physically inspect wiring and connections condition. Check terminals and cores for loose connections. |
| 2 | Visually inspect cabinet seals, glands, hinges, locks, switches, buttons and lamps condition. Test lamps |
| 3 | Visually inspect HV and LV terminal boxes, gaskets and internal connections. |

| FUN - Functional Tests |  |
| --- | --- |
| TASK | DESCRIPTION |
| 1 | Function test low oil level alarm. |
| 2 | Function test the Oil Temperature Indicator and Winding Temperature Indicator alarm and trip points. If transformer is Forced Air cooled, set the fans to "Auto" start. |
| 3 | Manually activate the micro switch on the Pressure Relief Valve |

| NOISE - Noise Inspections |  |
| --- | --- |
| TASK | DESCRIPTION |
| 1 | Listen to transformer for excessive/abnormal humming. |

| EARTH - Earthing System Inspections |  |
| --- | --- |
| TASK | DESCRIPTION |
| 1 | Visually inspect earth conductor, all earth connections inclusive of compound earthing connections and joins condition. |

| COOL - Cooling System Inspections |  |
| --- | --- |
| TASK | DESCRIPTION |
| 1 | Visually check cooling fins general condition and for oil leaks. |

| GEN - General Inspections |  |
| --- | --- |
| TASK | DESCRIPTION |
| 1 | Check general condition of the transformer compound, including fence. |

| IDS - Labelling and Identifications |  |
| --- | --- |
| TASK | DESCRIPTION |
| 1 | Visually check the identification (tag) label and the nameplate condition. |

| TEMP - Temperature Checks |  |
| --- | --- |
| TASK | DESCRIPTION |
| 1 | Check Oil Temperature, Winding Temperature and Oil Level. |

|  | Reading | Notes |
| --- | --- | --- |
| OTI |  |  |
| WTI |  |  |
| OL |  |  |